
[image: image1.png]Accessibility.com




Model

 SmartLift-S or EN
WORK BY OTHERS
PROJECT #: _______

PROJECT NAME: __________________

PROJECT MANAGER: ___________

REFER TO THIS DOCUMENT BEFORE

ANY INSTALLATION AND BEFORE

APPROVING THE FOLLOWING DRAWINGS

1. GÉNÉRALITY

1.1 Scopes

Furnish all labour, materials and equipment required to install an handicap hydraulic and cables (2:1) or screw drive platform lift commercial model SMARTLIFT for indoor application with a self supporting tower. The Smart lift is manufactured by Global Tardif Elevator Manufacturing Group inc. (here after called the Manufacturer) as shown on the drawings and specifications. 

The Manufacturer will supply shop drawings, materials and equipment to the installer company. Elevator construction works shall not start before drawings have been approved by owner or general contractor.
The Manufacturer is located at 120 de Naples, St-Augustin de Desmaures, Québec, Canada (T. 418 878 4116 or le 1.800.661.6316 ;  Fax 418.878.1595 ).

The hoistway for model SMARTLIFT-S shall be built by a general contractor 

The enclosure around the  SMARTLIFT-EN shall be provide by the manufacturer.

1.2 Preparatory work by others 

To complete the elevator installation, others works have to be done by others :

1. All masonry works, gyproc and paint.

2.  If hoistway is built by a general contractor (ref: SmartLift-S), it have to be built as per elevator shop drawings, (structural reinforcing, ventilation etc…) and follow all applicable codes and standards.
3. The pit depth is 3’’ (76 mm) minimum from first floor. The pit shall be clean and built as per code regulations. Provide pit waterproofing or sump pump if required. Provide adequate support for guide rail fastenings.
4. Provide level concrete pit floor to support loads impact of 3750 lbs (1705kg) as per chapter 1 of construction code.

5. Provide a lockable room to store elevator parts and equipment before and during installation.
6. Appropriate overhead from upper landing floor up to the hoistway ceiling as per elevation drawing from Global/Tardif.

7. During installation, hoistway landings access, to be fully open at least 8 feet high.

8. Cab floor finishing and installation by others (Maximum load: 2 lbs/square foot).

9. Rough openings for landing floor call stations and signage, as per drawings.

10. Electric power for setting and test on first installation day by electrical contractor.

11. As per National U.S. electric code or Canadian electric code, a fuse disconnect switch for each elevator connected on a 30 amps circuit equipped with a normally open type contact.

12. Following section 38 of electric Canadian codes, install an auxiliary contact in the principal disconnect switch.

13. The disconnect switch is install 20 feet (6 meters) away minimum from the controller and is visible from there. If not, a second disconnect switch shall be install near the controller.

14. Light, light switch and electric outlet in hoistway are required before starting elevator

            installation.

IMPORTANT
1. The elevator drawings are made in accordance of CAN-CSA-B355-00 codes.

2. These drawings are not done for the building construction. It is to illustrate the relation between the elevator and the structure.

3. This drawing is only for installation. The landing doors details and cab details will be on separates pages.

4. Global/Tardif is not responsible for the exact details and dimensions of the hoistway structure and the machine room.

5. The owner/buyer/builder will provide suitable lintels over and under landing entrances.

6. The doorframes are not built to support the weight of the walls. The general contractor is responsible for any damages caused by masonry and finishing works around the landing doors.

7. The total distance between the lower and the upper floor as per elevation drawing have to be maintain within ¼’’ (6mm).

8. Provide adequate support for guide rail fastenings or for towers supports as per shop drawings.

      9.   Provide finish grouting and masonry around doorframes only after the end of their

            installation.
